Only for ground water systems serving 4,900 people and under.

| Water System Name: |  | Plant: Address: |  |
| --- | --- | --- | --- |
| System#: |  |  |  |
| Contact: |  | Phone: |  |

Purpose: identify specific bacteriological sample locations which are representative of the water quality throughout the distribution system and to define actions required following a coliform-positive test result(s).

Population:             No. Connections                 A single distribution system (Yes or No)?

Source(s):                                                                         Well Tag#

1st Quarter	      2nd Quarter         3rd Quarter        4th Quarter

Months of Operation [circle]: (Jan  Feb  Mar  |  Apr  May  Jun  |  Jul  Aug  Sep  |  Oct  Nov  Dec)

#### Examples for quarterly: Closed in Summer – Jan – Mar; Apr – Jun; Late Aug – Sep; Oct – Dec [4 quarters]

Closed in Winter – Apr – Jun; Jul – Sep; Oct [3 quarters]

1. Number of bacteriological samples required            per  Quarter / Month / Year  [circle one].

2. The following have been identified as valid taps: (Example of Sampling Diagrams on back)

| Noncommunity |  | Community |
| --- | --- | --- |
| Finished Tap #1: |  | :Routine Tap [RTOR & RPOR] |
| Finished Tap #2: |  | : Upstream Tap [RPOT] |
| Finished Tap #3: |  | : Downstream Tap [RPOT] |
| Source Tap(s): |  | [raw water] |

- When coliform-positive routine samples occur, repeat samples must be collected within 24 hours.  Contact MDE for approval to delay repeat sampling.  Community and similar distribution systems - collect at least 1 each from the original tap, upstream tap, and downstream tap.

- Ground Water Rule - test for E. coli.  Triggered by a routine coliform-positive.

Treated Systems – at least 1 additional raw water sample from each source tap.

Untreated Systems – the above repeat closest to the well can also be used for Ground Water Rule.

- Next-month Routines - Whenever a coliform-positive routine occurs, and the system monitors less than monthly, at least three routine samples must be collected the following month.  A waiver may be granted by MDE, that must be requested by the system in writing, and include a probable cause of the positive and corrective actions taken.  System monitoring monthly are not required additional routines.

If E. coli contamination is confirmed, your consumers MUST be notified.  Contact MDE immediately.

If total coliform only contamination is confirmed, you must perform a Level 1 Assessment.

However, if it is the second such incident unresolved in a 12-month rolling period,

you must contact MDE to schedule a Level 2 Assessment.

Bacteriological Sample Siting Plan for Small Systems

Examples of Sampling Diagrams

Source Tap

Untreated System

Well 2

Tank

Source Tap

Treated System

Well 1

Tap #1

Tap #2

Tap #3

Tap #4

CAMPUS (MULTIPLE BUILDINGS)

Note that you may not be able to avoid dead ends, but be certain to select valid taps.

##### SMALL COMMUNITY (also campground or marina)

Source Tap

Untreated System

Backup Well

Tank

Source Tap

Treated System

Primary Well

Dead End

Dead End

Oak Lane

Maple Road

Pine Street

Squirrel Court

Lot 12

Tap #3

Tap #1

Lot 25

Tap #2

Lot 106

Tap #4

Lot 3

Note that the backup well must be sampled, if activated during routine sampling, and routines test positive.

- Please provide a diagram of your water system; include well locations and sample taps.  [Attachments welcome.]

- We recommend that you review the site plan with your sampler annually or whenever a new sampler is hired/contracted: (Taps should not be sprayed with bleach prior to sampling.)

(1) both a field pH and free chlorine test will be performed at the time of each sample;

(2) samples will be collected in sterile 100 mL sample bottle, preserved with thiosulfate;

(3) samples will be transported on ice and sealed from exposure to the ice;

(4) samples will be transported in a clean container, with ONLY other drinking water samples.

Please have your sampler initial below after reviewing plan, annually.  Keep for system records.

| 2016 |  | 2017 |  | 2018 |  | 2019 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2020 |  | 2021 |  | 2022 |  | 2023 |  |

Bacteriological Sample Siting Plan for Small Systems

Supplementary Page

| Water System Name: |  | System#: |  |
| --- | --- | --- | --- |

The following have been identified as valid taps: (Example of Sampling Diagrams Page 2)

| Noncommunity |  | Community |
| --- | --- | --- |

2(a). Source(s):                                                                         Well Tag#

| Finished Tap #1: |  | :Routine Tap |
| --- | --- | --- |
| Finished Tap #2: |  | : Upstream Tap |
| Finished Tap #3: |  | : Downstream Tap |
| Source Tap(s): |  |  |

2(b). Source(s):                                                                         Well Tag#

| Finished Tap #1: |  |  | :Routine Tap |
| --- | --- | --- | --- |
| Finished Tap #2: |  |  | : Upstream Tap |
| Finished Tap #3: |  |  | : Downstream Tap |
| Source Tap(s): |  |  |  |

2(c). Source(s):                                                                         Well Tag#

| Finished Tap #1: |  | :Routine Tap |
| --- | --- | --- |
| Finished Tap #2: |  | : Upstream Tap |
| Finished Tap #3: |  | : Downstream Tap |

2(d). Source(s):                                                                         Well Tag#

| Finished Tap #1: |  |  | :Routine Tap |
| --- | --- | --- | --- |
| Finished Tap #2: |  |  | : Upstream Tap |
| Finished Tap #3: |  |  | : Downstream Tap |
| Source Tap(s): | - |  |  |